## Read Me
Stairs Benchmark SB-1: Independent ACI 318-19 Hand Calculation vs Ñola Stairs Module
Purpose | Independent check of the Stairs module (engine stairs-0.1.0) on the MDM stair geometry with corrected design basis.
Code | ACI 318-19 (NSCP 2015 recorded as project standard). Combinations 1.2D + 1.6L and 1.4D.
Structure | Dog-leg, 2 × 13 risers, R 153.85, T 340, waist and landing 200 mm, B 1.8 m, mid landing 1,460 mm.
Supports | Flight 1: footing on soil (pinned) to landing beam (pinned). Flight 2: landing beam (pinned) to floor beam (fixed).
Method | Frame by force method / virtual work (hand.py, written separately from the module's stiffness solver); section checks as live Excel formulas from the ACI clauses; module values pasted from analyzeStairs().
Colour code | Blue = input · Black = Excel formula · Green = link to another sheet · Purple = value from hand.py or module output.
Not independent | Both use the same plan-load convention (steps to the last riser line) and the same thrust-envelope assumption; Findings 2 and 6 cover these.
Result
Values compared | 46
MATCH | 46
FLAG | 0
Largest ¦Δ¦ | 0.1547%
Sign-off | Engineer: ____________________ Date: __________ (review the Findings sheet first)

## Inputs
SB-1 Inputs (blue = input)
Item | Symbol | Value | Unit | Reference / formula | Note
Materials
Concrete strength | f'c | 27.6 | MPa | User
Rebar yield strength | fy | 414 | MPa | User (Grade 60 / PNS 49 Gr 415)
Rebar modulus | Es | 200000 | MPa | ACI 318-19 20.2.2.2
Concrete unit weight | γc | 24 | kN/m³ | Module default
Geometry
Floor to floor | H | 4000 | mm | MDM sheet
Risers per flight | n | 13 |  | MDM sheet (2 × 13)
Riser | R | 153.8462 | mm | H / (2n) = 153.85
Going (tread) | T | 340 | mm | MDM sheet
Waist thickness (normal to soffit) | t | 200 | mm | Assumed: MDM's 100 mm fails hmin
Landing thickness | tl | 200 | mm | Assumed
Mid-landing length (along run) | Ll | 1460 | mm | MDM sheet
Flight width | B | 1800 | mm | MDM sheet
Clear cover (top and bottom) | cc | 20 | mm | Agreed default
Support bearing width (all beams) | b | 250 | mm | Agreed default (250 × 500 beams)
Loads and combinations
Finishes on plan | SDL | 1 | kPa | Agreed default
Live load | L | 4.8 | kPa | NSCP 2015 Table 205-1 / ASCE 7 (stairs)
LC1 dead factor |  | 1.2 |  | ACI 318-19 Table 5.3.1 (5.3.1b)
LC1 live factor |  | 1.6 |  | ACI 318-19 Table 5.3.1 (5.3.1b)
LC2 dead factor |  | 1.4 |  | ACI 318-19 Table 5.3.1 (5.3.1a)
Reinforcement (module defaults)
B1 main bottom: bar | db | 12 | mm
B1 main bottom: spacing | s | 150 | mm
T1 top at bottom support: bar | db | 12 | mm
T1 top at bottom support: spacing | s | 300 | mm
T2 top at top support: bar | db | 12 | mm
T2 top at top support: spacing | s | 300 | mm
T3 top at knees / landing: bar | db | 12 | mm
T3 top at knees / landing: spacing | s | 200 | mm
D1 distribution: bar | db | 10 | mm
D1 distribution: spacing | s | 200 | mm
Bottom-bar extension past knee |  | 600 | mm | Module default
T3 top-bar extension each side of knee |  | 700 | mm | Module default
Supports and footing
Bottom of flight 1 |  | Footing on soil, pinned |  | User
Mid landing far edge |  | Landing beam, pinned |  | User
Top of flight 2 |  | Floor beam, fixed |  | User
Allowable bearing | qa | 150 | kPa | Agreed default
Footing width (along run) | Bf | 600 | mm | Module default
Footing thickness | hf | 300 | mm | Module default
Soil above footing (base 1.0 m below grade) |  | 700 | mm | Agreed default
Soil unit weight | γs | 18 | kN/m³ | Module default
Base friction coefficient | μ | 0.45 |  | Module default
Footing cover |  | 75 | mm | ACI 318-19 20.5.1.3.1 (cast against earth)
Footing bars: diameter |  | 12 | mm
Footing bars: spacing |  | 200 | mm

## Loads
Loads on Plan (per 1 m strip)
Item | Symbol | Value | Unit | Reference / formula | Note
Pitch
Pitch angle | θ | 24.3462 | deg | atan(R/T)
cos θ |  | 0.91107
tan θ |  | 0.45249
Dead load
Waist γc·t/cosθ |  | 5.2685 | kPa | Slab on slope converted to plan
Steps γc·R/2 |  | 1.8462 | kPa | Triangular steps, average depth R/2
Flight dead load | wD,f | 8.1147 | kPa | Waist + steps + finishes
Landing dead load | wD,l | 5.8 | kPa
Factored (governing LC1)
Flight wu |  | 17.4176 | kPa | 1.2D + 1.6L
Landing wu |  | 14.64 | kPa | 1.2D + 1.6L
Plan load regions (convention)
Flight 1: steps end at last riser line (n−1)T |  | 4080 | mm | Landing top is the last tread
Flight 1 strip span on plan | L1 | 5540 | mm | Bottom pin to landing beam
Flight 2 strip span on plan | L2 | 5880 | mm | Landing beam to top beam

## Frame
Frame Analysis: Force Method (Virtual Work), Independent of the Module Solver
Item | Symbol | Value | Unit | Reference / formula | Note
Method
Model |  | Centreline frame |  | Waist line parallel to pitch line at t/(2cosθ) below it; landing at tl/2 below its top; knee at the intersection
Solution |  | Force method |  | Primary structure pin + roller; redundants by δ10 + Σ Xj δ1j = 0, δ = ∫M m/EI ds + ∫N n/EA ds (gross EcIg, Ec = 4700√f'c), 3,000 segments per member | Script hand.py (purple values)
Thrust envelope |  | Both cases |  | Horizontal restraint at both supports (restrained) and released at the second support (released); results enveloped, as in the module
Excel closed-form check: flight 1 strip, horizontal restraint released (simply supported on plan)
Left reaction under LC1 | RA | 47.7124 | kN/m | Moments about the landing beam
Zero shear from left | x0 | 2.7393 | m | Within flight (x0 < xe1)
Mu+ max (released case) | Mu+ | 65.3498 | kN·m/m | RA·x0/2
Knee x (flight 1) |  | 4441.5716 | mm | Centreline intersection
Flight 1 strip (pinned footing, pinned landing beam)
Footing: dead vertical (service) |  | 51.2417 | kN/m | Restrained case (larger)
Footing: live vertical (service) |  | 31.5809 | kN/m
Footing: service thrust H (restrained) |  | 130.9195 | kN/m | D + L
Footing: factored V max |  | 112.0194 | kN/m | Envelope
Footing: factored ¦H¦ max |  | 177.2646 | kN/m
Landing beam: dead vertical |  | 19.5441 | kN/m | Released case (larger)
Landing beam: live vertical |  | 13.296 | kN/m
Landing beam: factored V min (uplift if < 0) |  | -19.5803 | kN/m | Restrained case, LC2/LC1
Mu+ max, waist |  | 65.3505 | kN·m/m | at x = 2.74 m (released case)
Mu+ max, landing |  | 40.2917 | kN·m/m | at the knee
Mu− max, knee |  | -30.3329 | kN·m/m | Restrained case (thrust)
Vu max outside support zones (b/2 + d) |  | 40.5675 | kN/m | at x = 4.44 m (knee)
Max axial tension |  | 11.8002 | kN/m
Flight 2 strip (pinned landing beam, fixed top beam)
Landing beam: dead vertical |  | 15.1539 | kN/m | Released case (larger)
Top beam: dead vertical |  | 45.4275 | kN/m | Restrained case (larger)
Top beam: live vertical |  | 27.8829 | kN/m
Top beam: factored fixed-end ¦M¦ |  | 73.5636 | kN·m/m | Released case governs (1.2·33.77 + 1.6·20.68)
Mu+ max, landing |  | 35.9871 | kN·m/m | at the knee
Mu+ max, waist |  | 41.1349 | kN·m/m | at x = 2.25 m
Mu− at knee (landing side) |  | -17.1963 | kN·m/m
Vu max outside support zones |  | 52.8313 | kN/m | at x = 5.58 m (b/2 + d from top beam)
Max axial tension (at top beam) |  | 155.4631 | kN/m | Released case

## Sections
Section Capacities and Detailing (ACI 318-19)
Item | Symbol | Value | Unit | Reference / formula | Note
Effective depth, 12 mm bars | d | 174 | mm | h − cc − db/2
β1 |  | 0.85 |  | Table 22.2.2.4.3
B1: Ø12 flexure (Whitney block)
As per metre | As | 753.9822 | mm²/m
Block depth | a | 13.3056 | mm | 22.2.2.4.1
Steel strain | εt | 0.030347 |  | 22.2.1.2
φ |  | 0.9 |  | Table 21.2.2
φMn |  | 47.0135 | kN·m/m | 22.2
T1: Ø12 flexure (Whitney block)
As per metre | As | 376.9911 | mm²/m
Block depth | a | 6.6528 | mm | 22.2.2.4.1
Steel strain | εt | 0.063694 |  | 22.2.1.2
φ |  | 0.9 |  | Table 21.2.2
φMn |  | 23.974 | kN·m/m | 22.2
T2: Ø12 flexure (Whitney block)
As per metre | As | 376.9911 | mm²/m
Block depth | a | 6.6528 | mm | 22.2.2.4.1
Steel strain | εt | 0.063694 |  | 22.2.1.2
φ |  | 0.9 |  | Table 21.2.2
φMn |  | 23.974 | kN·m/m | 22.2
T3: Ø12 flexure (Whitney block)
As per metre | As | 565.4867 | mm²/m
Block depth | a | 9.9792 | mm | 22.2.2.4.1
Steel strain | εt | 0.041463 |  | 22.2.1.2
φ |  | 0.9 |  | Table 21.2.2
φMn |  | 35.6106 | kN·m/m | 22.2
One-way shear, Table 22.5.5.1(c)
Size effect λs |  | 1 |  | 22.5.5.1.3
√f'c (≤ 8.3) |  | 5.2536 | MPa | 22.5.3.1
φVc with B1 (ρw from bottom bars), Nu = 0 |  | 73.77 | kN/m | φ = 0.75
φVc with T3, Nu = 0 |  | 67.0245 | kN/m | Knee hogging zone
φVc with T2, Nu = tension at top beam |  | 41.6447 | kN/m | Nu/(6Ag) term with tension (conservative: max Nu)
Minimum steel, spacing, crack control
ρ min (fy < 420 → 0.0020) |  | 0.002 |  | Table 24.4.3.2 / 7.6.1.1
As,min = ρmin·b·h |  | 400 | mm²/m
s max, main bars |  | 450 | mm | 7.7.2.3
fs = 2/3 fy |  | 276 | MPa | 24.3.2.1
Crack-control spacing |  | 304.3478 | mm | Table 24.3.2
Development
ld, Ø12 bottom (cb = cc + db/2) | ld | 317.4185 | mm | 25.4.2.4, ψs 0.8, Ktr 0
ld, Ø12 top bar (ψt 1.3) at fixed end |  | 412.6441 | mm | Module applies ψt = 1.3 conservatively
ψc |  | 0.86286 |  | Table 25.4.3.2
ldh, Ø12 standard hook (ψr 1.6, ψo 1.25) | ldh | 245.7869 | mm | 25.4.3.1(a)

## Serviceability
Minimum Thickness and Deflection
Item | Symbol | Value | Unit | Reference / formula | Note
Minimum thickness, Table 7.3.1.1 on developed length
fy factor 0.4 + fy/700 |  | 0.99143 |  | 7.3.1.1.1
Flight 1 strip developed length |  | 5973.5384 | mm | Centreline, from Frame model
hmin flight 1 (simply supported, ℓ/20) |  | 296.1168 | mm
Flight 2 strip developed length |  | 6309.3272 | mm
hmin flight 2 (one end continuous, ℓ/24) |  | 260.6353 | mm | Fixed top
Effective inertia, Table 24.2.3.5 (B1 bottom bars, governing sagging)
Ec = 4700√f'c |  | 24691.78 | MPa | 19.2.2.1(b)
n = Es/Ec |  | 8.0999
Ig per metre |  | 666666666.6667 | mm⁴
Cracked neutral axis |  | 40.3965 | mm
Icr |  | 130986061.2985 | mm⁴
Mcr = fr Ig / yt |  | 21.7148 | kN·m/m | 19.2.3.1
Ma flight 1 strip (max service D+L) |  | 48.3212 | kN·m/m | From Frame model
Ie/Ig flight 1 strip |  | 0.21175 |  | Ie applied to the whole span
Ma flight 2 strip (max service D+L) |  | 30.3826 | kN·m/m | From Frame model
Ie/Ig flight 2 strip |  | 0.24032 |  | Ie applied to the whole span
Deflection by virtual work with EcIe (envelope of both thrust cases)
Flight 1: immediate live ΔL |  | 18.4693 | mm | Unit load scanned at 111 points
Flight 1: long-term λΔ·ΔD + ΔL (λΔ = 2.0, ψ = 0) |  | 78.0994 | mm | 24.2.4.1
Flight 1: limit ℓ/360 |  | 15.3889 | mm | Table 24.2.2
Flight 1: limit ℓ/240 |  | 23.0833 | mm | Table 24.2.2
Flight 2: immediate live ΔL |  | 8.5367 | mm | Unit load scanned at 111 points
Flight 2: long-term λΔ·ΔD + ΔL (λΔ = 2.0, ψ = 0) |  | 35.8717 | mm | 24.2.4.1
Flight 2: limit ℓ/360 |  | 16.3333 | mm | Table 24.2.2
Flight 2: limit ℓ/240 |  | 24.5 | mm | Table 24.2.2

## Footing
Footing Under the Bottom Support (Strip Footing per m)
Item | Symbol | Value | Unit | Reference / formula | Note
Stair service reaction D + L |  | 82.8226 | kN/m | Frame (restrained case)
Footing weight |  | 4.32 | kN/m
Soil on footing (outside the seat) |  | 4.41 | kN/m
Total P |  | 91.5526 | kN/m
Eccentricity e = H·hf / P |  | 0.429 | m | Pinned seat, M = 0
Kern limit Bf/6 |  | 0.1 | m
q max (∞ if e ≥ Bf/2) |  | Outside | kPa | Resultant outside the footing
Sliding μP/H |  | 0.31469 |  | Required 1.5
Footing d |  | 219 | mm
Footing φMn (Ø12 @ 200) |  | 45.0921 | kN·m/m | Tension-controlled (εt large)
As,min = ρmin·b·hf |  | 600 | mm²/m
As provided |  | 565.4867 | mm²/m
Hook space available hf − cover − Ø |  | 213 | mm

## Comparison
Hand Calculation vs Module (engine stairs-0.1.0)
Tolerance: ±2% forces/deflections, ±1% capacities and code limits. Module values are pasted from analyzeStairs() output.
# | Quantity | Unit | Hand | Module | Δ % | Tol % | Status | Module source
Loads
1 | Flight dead load on plan | kPa | 8.1147 | 8.1147 | 0% | 2% | MATCH | result.loads.flight.total
2 | Landing dead load | kPa | 5.8 | 5.8 | 0% | 2% | MATCH | result.loads.landings[0].dead
3 | Pitch angle θ | deg | 24.3462 | 24.3462 | 0% | 1% | MATCH | result.pitch.degrees
Flight 1 strip
4 | Footing dead reaction | kN/m | 51.2417 | 51.2408 | -0.001633% | 2% | MATCH | strips[0].reactions[0].dead.v
5 | Footing live reaction | kN/m | 31.5809 | 31.5809 | 8.034e-05% | 2% | MATCH | strips[0].reactions[0].live.v
6 | Footing service thrust H | kN/m | 130.9195 | 130.9178 | -0.001292% | 2% | MATCH | strips[0].reactions[0].service.h
7 | Footing factored V max | kN/m | 112.0194 | 112.0185 | -0.0008599% | 2% | MATCH | factored.vMax
8 | Footing factored ¦H¦ max | kN/m | 177.2646 | 177.2626 | -0.001129% | 2% | MATCH | factored.hAbsMax
9 | Landing beam dead reaction | kN/m | 19.5441 | 19.5435 | -0.002824% | 2% | MATCH | strips[0].reactions[1].dead.v
10 | Landing beam live reaction | kN/m | 13.296 | 13.296 | 6.79e-09% | 2% | MATCH | strips[0].reactions[1].live.v
11 | Landing beam factored V min (uplift) | kN/m | -19.5803 | -19.5802 | 0.000326% | 2% | MATCH | factored.vMin
12 | Mu+ waist (Excel closed form, released case) | kN·m/m | 65.3498 | 65.35 | 0.0002893% | 2% | MATCH | check s1:flight-1:flexure-pos
13 | Mu+ waist (force method) | kN·m/m | 65.3505 | 65.3459 | -0.006931% | 2% | MATCH | max station mPos
14 | Mu− knee | kN·m/m | -30.3329 | -30.3394 | -0.02125% | 2% | MATCH | min station mNeg
15 | Vu max outside support zones | kN/m | 40.5675 | 40.5863 | 0.04615% | 2% | MATCH | max station vu, ¦x − xs¦ ≥ b/2 + d
Flight 2 strip
16 | Landing beam dead reaction | kN/m | 15.1539 | 15.1537 | -0.001529% | 2% | MATCH | strips[1].reactions[0].dead.v
17 | Top beam dead reaction | kN/m | 45.4275 | 45.4271 | -0.0008403% | 2% | MATCH | strips[1].reactions[1].dead.v
18 | Top beam live reaction | kN/m | 27.8829 | 27.8829 | -7.465e-05% | 2% | MATCH | strips[1].reactions[1].live.v
19 | Top beam factored fixed-end ¦M¦ | kN·m/m | 73.5636 | 73.6096 | 0.06258% | 2% | MATCH | factored.mAbsMax
20 | Mu+ landing (at knee) | kN·m/m | 35.9871 | 35.99 | 0.008153% | 2% | MATCH | check s2:mid-landing:flexure-pos
21 | Mu+ waist | kN·m/m | 41.1349 | 41.13 | -0.01199% | 2% | MATCH | check s2:flight-2:flexure-pos
22 | Mu− knee (landing side) | kN·m/m | -17.1963 | -17.2 | -0.02145% | 2% | MATCH | check s2:mid-landing:flexure-neg:topKnee
23 | Vu max outside support zones | kN/m | 52.8313 | 52.8559 | 0.04656% | 2% | MATCH | max station vu
24 | Max axial tension | kN/m | 155.4631 | 155.4723 | 0.005965% | 2% | MATCH | max station nuTension
Section capacities
25 | φMn B1 Ø12 @ 150 | kN·m/m | 47.0135 | 47.01 | -0.007415% | 1% | MATCH | check detail
26 | φMn T2 Ø12 @ 300 | kN·m/m | 23.974 | 23.97 | -0.01665% | 1% | MATCH | check detail
27 | φMn T3 Ø12 @ 200 | kN·m/m | 35.6106 | 35.61 | -0.001546% | 1% | MATCH | check detail
28 | εt B1 |  | 0.030347 | 0.0303 | -0.1547% | 1% | MATCH | check detail (4 d.p.)
29 | As,min | mm²/m | 400 | 400 | 0% | 1% | MATCH | bars:mainBottom:minimum
30 | Crack-control spacing | mm | 304.3478 | 304 | -0.1143% | 1% | MATCH | bars:mainBottom:crack
31 | ld Ø12 bottom | mm | 317.4185 | 317 | -0.1318% | 1% | MATCH | detail:knee-bottom
32 | ld Ø12 top (ψt 1.3) | mm | 412.6441 | 413 | 0.08626% | 1% | MATCH | detail:top-anchorage
33 | ldh Ø12 | mm | 245.7869 | 245.7869 | 0% | 1% | MATCH | footing.dowelRequired
Serviceability
34 | hmin flight 1 | mm | 296.1168 | 296.1168 | -5.376e-07% | 1% | MATCH | spans[0].hmin
35 | hmin flight 2 | mm | 260.6353 | 260.6353 | -5.586e-07% | 1% | MATCH | spans[0].hmin
36 | Mcr | kN·m/m | 21.7148 | 21.7148 | 0% | 1% | MATCH | spans[0].mcr
37 | Ie/Ig flight 1 |  | 0.21175 | 0.21175 | 0.001387% | 1% | MATCH | spans[0].ieRatio
38 | Ie/Ig flight 2 |  | 0.24032 | 0.24033 | 0.00577% | 1% | MATCH | spans[0].ieRatio
39 | ΔL flight 1 | mm | 18.4693 | 18.469 | -0.00152% | 2% | MATCH | spans[0].immediateLive
40 | Δ long-term + L, flight 1 | mm | 78.0994 | 78.0999 | 0.0006733% | 2% | MATCH | spans[0].total
41 | ΔL flight 2 | mm | 8.5367 | 8.5371 | 0.004081% | 2% | MATCH | spans[0].immediateLive
42 | Δ long-term + L, flight 2 | mm | 35.8717 | 35.8639 | -0.02169% | 2% | MATCH | spans[0].total
Footing
43 | Total service P | kN/m | 91.5526 | 91.5518 | -0.000886% | 2% | MATCH | footing.serviceP
44 | Eccentricity | m | 0.429 | 0.429 | -0.0004061% | 2% | MATCH | footing.eccentricity
45 | Sliding μP/H |  | 0.31469 | 0.31469 | 0.0004061% | 2% | MATCH | footing.slidingFs
46 | Footing φMn | kN·m/m | 45.0921 | 45.0921 | 0% | 1% | MATCH | footing.phiMn
| Values compared |  | 46
| MATCH |  | 46
| FLAG |  | 0
| Largest ¦Δ¦ |  | 0.1547%

## Findings
Findings From the Benchmark (for engineer review)
# | Type | Finding | Evidence | Recommendation | Your decision
1 | Module issue | One-way shear reports φVc = 0 (DCR ∞) at a station where the governing combination has a tiny hogging moment and no top bars exist (ρw = 0). | s1:flight-1:shear: Vu 29.61 kN/m at x = 3.69 m, Mu− only −1.29 kN·m/m; s2:flight-2:shear same at x = 5.13 m. Real governing shear: flight 1 Vu 40.6 vs φVc 67.0 (T3) → 0.61; flight 2 Vu 52.8 at b/2 + d from the top beam vs φVc 41.6 (T2 Ø12 @ 300 with Nu tension 155 kN/m) → 1.27, a genuine shear failure that the ∞ result hides. | Take ρw from the bars actually in tension at that station; where the hogging zone has no top bars, use the bottom bars when ¦Mu−¦ < Mcr (section uncracked in hogging), else keep the 'no top bars' flag in flexure only. Fix in v1.1.
2 | Modelling decision | Thrust envelope keeps the horizontal restraint at the FIRST support. For flight 1 that is the footing on soil, which then carries 131 kN/m service thrust: resultant outside the 600 mm footing, sliding FS 0.31. | footing:bearing 'Resultant outside footing', footing:sliding DCR 4.77. Hand calc reproduces H = 130.92 kN/m exactly, so the arithmetic is right; the assumption is the issue. | When the bottom support is on ground, release the horizontal restraint at the footing (soil cannot take thrust) and let the landing beam / floor diaphragm carry it; check the footing for vertical load and friction only.
3 | Modelling consequence | In the restrained case the landing beam (pinned) takes 131 kN/m horizontal thrust and −19.6 kN/m factored uplift. | strips[0].reactions[1].factored.vMin = −19.58 (hand −19.58). | Report the landing-beam thrust and uplift in the reactions table so the beam is designed for them (currently a warning only).
4 | Design result (inputs) | Default bars fail for this geometry: B1 Ø12 @ 150 (DCR 1.39), T2 Ø12 @ 300 at fixed top (3.07); h = 200 < hmin and long-term deflection 78 mm > ℓ/240. | Matches hand calc; this is the design, not the software. | Not a software issue. Benchmark keeps module default bars so all checks are exercised.
5 | Code note | fy = 414 MPa (Grade 60) falls in the fy < 420 row of Table 24.4.3.2 → ρmin 0.0020 and hmin factor 0.991. | Literal reading of ACI 318-19 SI tables; same in hand calc. | Keep. Optionally treat 414 as Grade 420 (US Grade 60) to get 0.0018; your call.
6 | Convention | Steps' self-weight is applied up to the last riser line; between the last riser and the knee the landing load is used (concrete there is ~370 mm deep). | Effect ≈ 0.8 kN per metre strip (< 1% of span load). Hand calc uses the same textbook convention, so this benchmark does not test it. | Accept (standard practice).